RENSON LOUVRE SPECIFICATIONS

Brand		: LOUVRE PANEL

Type 		: 428 – GLAZED-IN 33mm pitch wall louvre

Manufacture and reference :

The 428 Louvre Panel is manufactured and supplied by Renson Fabrication Ltd.  Tel: 01622 754123

Email: louvres@rensonuk.net Website: www.renson.eu

Description:

RENSON 428 is a high duty extruded aluminium louvre panel using a L.033V pitch blade mounted into an integrated frame. It is designed to be glazed into a pre formed opening and the chevron blades provide private ventilation which cannot be seen through from either side.

System operation and performance:

Type				428

Visual Free Area		59%

Physical Free Area		43%

K-factor: Intake			61.04

K-factor: Discharge		61.04

Ce coefficient: Intake		0.128

Cd coefficient: Discharge	0.128

Watertightness (HEVAC) – Class A (with water channel) at 0.5m/s

Dimensions/Size Range:

Minimum Dimensions (mm)	220 x 220

Thickness (mm)		24 or 32

Pitch (mm)			33

Product Construction:

Profile: Extruded aluminium (EN 12020-2)

Surface Treatment:

Mill finish

Anodised (EV6/EV1) (20 micron): pre-treated and anodised.

Polyester powder coating in any RAL colour (40 micron): aluminium profiles pre-treated to resist corrosion to guarantee.

Installation:

To be fitted like double glazing

Accessories

Stainless steel birdguard 6mm x 6mm secured to the rear

Stainless steel insect mesh 2.3mm x 2.3mm secured to the rear

Water channel

Product Information:

http://www.rensonuk.net/Louvres-panels-United-Kingdom.html