specification sheet

464 incendo®

LOUVRE - transit vent

manufacturer

RENSON Ventilation, IZ 2 Vijverdam, Maalbeekstraat 10, 8790 Waregem – Belgium

tel. +32 (0)56 62 71 11, fax. +32 (0)56 60 28 51, info@renson.be  www.renson.eu

series

AESTHETIC

FIRE-RESISTANT

built-in

WALL/FLOOR/CEILING/DOOR LOUVRE

WITH v-BLADES

types

464 Incendo®

description

The fire-resistant 464 Incendo® louvre is an aesthetic louvre consisting of V-blades supplied as standard in a rigid frame with adjustable counter-frame that can be installed in fire doors, solid walls, ceilings, floors and flexible walls.

The blades are made of thermally expandable Palusol® strips covered in laminated polystyrene sleeves. The distance between the blades is 20 mm.

Both the frame and counter-frame are made of laminated polystyrene. The louvre is always square or rectangular.

Minimum dimensions are 100 x 100 mm (W x H) and maximum dimensions 800 x 400 mm (W x H). Other dimensions are available upon request.

The blades are V-shaped, allowing no see-through visibility. The aesthetic design of the louvre makes cover grilles unnecessary. The blades, frame and counter-frame have the same finish. The standard colours are glossy white (approx. RAL 9016), light aluminium grey (approx. RAL 9022) and anthracite grey (approx. RAL 7024). Other colours or woodgrain finishes are available upon request. No vertical posts are visible.

The fire-resistant 464 Incendo® louvre requires no maintenance and has no mechanical parts.

At normal ambient temperatures, the 464 Incendo® allows ventilation between two adjacent rooms. In case of fire (100°C and up), the blades expand, blocking ventilation and preventing the spread of the fire. No toxic hydrogen chloride is released in a fire.

The 464 Incendo® has been tested and conforms to the applicable standards.

Fire classification is in accordance with NBN EN13501-2; fire testing was carried out in accordance with: EN 1364-1 (partition walls), EN 1364-2 (independent suspended ceilings), EN 1634-1 (fire-resistant doors and gates). Test and classification reports are available upon request.

The fire-resistant 464 Incendo® louvre has a visual free area of 61% and a physical free area of 51%.

Fire-resistance classes are: EI60 / EW90 (ve i↔o) when installed in a massive wall (100 mm concrete), EI60 (ho i↔o) in a massive floor (100 mm concrete), EI60 (ve i↔o) in a flexible wall (100 mm metal stud and gypsum plasterboard), EI60 / EI30 / EW60 / EW30 (ve i↔o) in a wooden door panel (50 mm or larger), EI30 / EW30 (ve i↔o) in a wooden door panel (40 mm or larger).

The fire-resistance of the structural elements in which the louvre is located must be at least the same as that of the louvre.

The unit must be installed according to the instructions and with the blades kept horizontal, using mastic cement (and, depending on the installation, in a calcium silicate frame). The unit must be attached in such a way as to guarantee mechanical stability.

Contact with water must be avoided and the louvre may not be used outdoors.

The louvre is optionally available without a frame or without a counter-frame.

material & finish

Blades: Polystyrene sleeves filled with Palusol

Frame profile: Polystyrene

Finish: glossy white (approx. RAL 9016), light aluminium grey (approx. RAL 9022), anthracite grey

(approx. RAL 7024), other colours upon request.

Note: louvre is not suitable for outdoor use and is not water-resistant

dimensions

Fitted depth		: variable

Blade pitch		: 20 mm

Flange size		: 14 mm

Total thickness		: 59 mm

Minimum dimensions	: 100 mm x 100 mm (W x H)

Maximum dimensions	: 800 mm x 400 mm (W x H)

INSTALLATION

By accredited installer, following installation instructions, with mastic cement, blades always horizontal

- In a massive wall (100 mm concrete)

- In a massive floor/ceiling (100 mm concrete)

- In a flexible wall (100 mm metal stud and gypsum plasterboard)

- In a (fire-resistant) wooden door panel (40 mm thickness or more)

optional extras

Frame – counter-frame: The 464 louvre comes standard with a frame and adjustable counter-frame. It is optionally available without a counter-frame and without a frame and counter-frame.

Technical specifications

464

Airflow:

- K-factor, supply: 10,27

- K-factor, extraction: 10.27

- Ce coefficient: 0,312

- Cd coefficient: 0,312

Free area:

- Visual free area  61%

- Physical fee area  51%

Sound reduction Rw (C;Ctr):

- Open:	3 (0;0) dB

Fire-resistance as per EN13501-2

- massive wall (100 mm concrete): 				EI60 / EW90 (ve i↔o)

- massive floor (100 mm concrete):				EI60 (ho i↔o)

- flexible wall (100 mm metal stud and plasterboard):		EI60 (ve i↔o)

- wooden door panel (50 mm):		EI60 / EI30 / EW60 / EW30 (ve i↔o)

- wooden door panel (40 mm):				EI30 / EW30 (ve i↔o)

standards

This product is manufactured according to, complies with and/or has been tested according to:

NBN EN13501-2

EN 1364-1

EN 1364-2

EN 1634-1

EN ISO 140-10

EN ISO 717-1

EN 13141-1