specification sheet

467

LOUVRE - transit vent

manufacturer

RENSON Ventilation, IZ 2 Vijverdam, Maalbeekstraat 10, 8790 Waregem – Belgium

tel. +32 (0)56 62 71 11, fax. +32 (0)56 60 28 51, info@renson.be  www.renson.eu

series

FIRE-RESISTANT

built-in

WALL LOUVRE

WITH  HORIZONTAL BLADES

types

467

description

The fire-resistant 467 louvre is a rectangular linear bar louvre ensuring 120 minutes fire resistance in rigid walls.

The blades are made of thermally expandable Palusol® strips covered in laminated polystyrene sleeves. The distance between the blades is 20 mm.

The frame is made of HDF. The louvre is always square or rectangular.

Minimum dimensions are 150 x 100 mm (W x H) and maximum dimensions 1200 x 800 mm (W x H).

Color grey.

The fire-resistant 467 louvre requires no maintenance and has no mechanical parts.

At normal ambient temperatures, the 467 allows ventilation between two adjacent rooms. In case of fire (100°C and up), the blades expand, blocking ventilation and preventing the spread of the fire. No toxic hydrogen chloride is released in a fire.

The 467 has been tested and conforms to the applicable standards.

Fire classification is in accordance with NBN EN13501-2; fire testing was carried out in accordance with: EN 1364-1 (partition walls). Classification report is available upon request.

The fire-resistant 467 louvre has a visual free area of 66,7% and a physical free area of 66,7%.

Fire-resistance classes are: EI120 (ve i↔o) when installed in a massive wall (100 mm concrete).

The fire-resistance of the structural elements in which the louvre is located must be at least the same as that of the louvre.

The unit must be installed according to the instructions and with the blades kept horizontal, using gypsum or Ytocol. The unit must be attached in such a way as to guarantee mechanical stability.

Contact with water must be avoided and the louvre may not be used outdoors.

material & finish

Blades: Polystyrene sleeves filled with Palusol

Frame profile: HDF

Finish: colour grey

.

Note: louvre is not suitable for outdoor use and is not water-resistant

dimensions

Fitted depth		: 100 mm

Blade pitch		: 18 mm

Total thickness		: 100 mm

Minimum dimensions	: 150 mm x 100 mm (W x H)

Maximum dimensions	: 1200 mm x 800 mm (W x H)

INSTALLATION

By accredited installer, following installation instructions, with gypsum or Ytocol, blades always horizontal

- In a massive wall (100 mm concrete)

Technical specifications

Airflow:

- K-factor, supply: 4,16

- K-factor, extraction: 4,06

- Ce coefficient: 0,49

- Cd coefficient: 0,496

Free area:

- Visual free area  66,7%

- Physical fee area  66,7%

Fire-resistance as per EN13501-2

- massive wall (100 mm concrete): 				EI120 (ve i↔o)

standards

This product is manufactured according to, complies with and/or has been tested according to:

NBN EN13501-2

EN 1364-1

EN 1364-2

EN 1634-1